March 18, 2019
Keith Dylewski  PE

Civ Pro Engineering
4450 Belden Village Street NW
Canton, OH  44718
RE:
Tiger Tarps Site Plan Review
Mr. Dylewski:
The City of Massillon Engineering Department has reviewed the submitted site plan for the above referenced project.  The following comments have been compiled for the site plan.  I did not create a redline mark up set.  In your re-submittal provide a response letter addressing each comment and three (3) revised sets of plans and if applicable two (2) copies of supporting documentation.
GENERAL
1) Provide a letter from the Stark County Sanitary Engineer to allow sanitary sewer connection into the manhole at intersection of 9th Street SW and Sanders Ave.  (county trunk sewer)
2) Provide replat/dedication plat?  And sewer easement dedication plat.
3) Label the R/W width and pavement width at the front of the site (typical all sheets)

4) Change 8” flowline to 6” on the lateral side of Manhole #WWS-2  (sheet 5 of 6 on sewer extension plans and sheet 6 of 9 on site plan)
TITLE SHEET
5) Add note and signature block for review of ESC plan……… “Approved by Stark Soil and Water District by letter dated ____________”.

SHEET 3 EXISTING CONDITIONS
6) Label the existing zoning of the site parcel
7) Label the names, lot numbers, and zoning for all adjacent parcels

SHEET 4  SITE PLAN

8) Label the total area of proposed pavement
9) Provide a letter requesting a variance of hard surface parking area (Section 1183) and why it is necessary
10) Note how parking spaces were calculated based on zoning code.  Number required / provided based on employee count, sf, etc.
11) Label the total disturbed area for the site including the sanitary sewer installation.

12) Show and label site sign, lighting, and any fencing.

SHEET 5  GRADING PLAN

13) Provide the flood zone and map number information on this sheet.
SHEET 6  UTILITY  PLAN/ SEWER PLAN
14) Add a note to core drill existing manhole and bench as needed to install new 8-inch PVC sewer pipe
15) No storm sewer on site?  Water is not to sheet flow to 9th street.  Add structures.
SHEET 7  DETAILS

16) Provide City of Massillon driveway detail on the plans (see attached)
 STORM WATER MANAGEMENT REPORT

17) Provide a storm water management design and report as shown on the site plan checklist.  Some effort should be made.
If you have any questions or require additional information, please contact our office at 330-830-1722.

Respectfully,
Jason M. Popiel,  P.E., CPESC
CITY ENGINEER
Jason Haines

Engineering Technician
(Enclosures)
